March 3, 2011

General (Assumptions/Decisions):

Key points:

- Minimum air velocity in the exhaust piping of 15-20 M/sec. To prevent soot build up on the piping walls

- Pressure of -15000pa

- 800 cubic Meters/Hour flow
Duty Cycle: Continuous Duty 24/7 operation
Operators / openings: 8 (12 if counting chamber exhaust openings on needle machine)

Remote on / off
No exhaust in cleanroom
Exhaust / vacuum system location - Mezzanine / outside clean room

Flow sensor and location for filter condition monitoring?

Noise level for exhaust?

Spare (backup) system?

Needle Assembly:

4 welds – opening / exhaust for each weld point

4 station / chamber – opening for each station / chamber

Weld chamber exhaust is not control / monitored. The

laser / process exhaust can be controlled manually and the 
flow is measured by a sensor IFM SI5002. At every station 
the chamber exhaust tube and the laser / process exhaust 
tube is combined at the top of the station to one stainless 
steel tube with outer diameter of 40 mm.

VG Setting (Injector):
3 welds – Opening / exhaust for each weld point
Opening diameters:

- St40: 16mm

- St70 and 90: 20mm

From the point of use ~ 1m steel pipe then flex tubing (type: Superflextract - soft 41mm):

- St40: ~1.8m

- St70: ~1.5m

- St90: ~1m

The valve at the top of the station used to regulate flow: IFM SD9000 DN40/PN16

Fitting size of the valve: PN16

March, 2011 – possible two additional pickup points for tray cleaning/blow off. 
       - Amtech, A C E  3/3/2011
       - Ruwac 3/10/2011

Final Assembly (Injector):
1 Laser marking - Opening / exhaust