Wolf-tec Site Visit Report - 3/13/15

- Arrived at the job site at 1:00pm 3/12/15

- Plant maintenance showed me the problem with the outlets.

- I checked the supply fuses for the two outlets that were not working and found that the fuses had blown.

- Replaced fuses and outlets had 118 volts across the hot and neutral.

- With the fuse out of the circuit (as if blown) we would get a reading of approximately 190 volts AC.  If a tool was plugged into the outlet, the tool would not operate.

- Sent an e-mail to Taiwan and they stated that the circuit should have an “Earth Leakage Circuit Breaker” installed to remove this “leakage voltage”.

- While inspecting the panels we found that the din rail on top of three of the transformers was badly damaged and all the terminal blocks were loose. Worked with plant maintenance to replace the damaged din rail.

- During panel inspection we found that the breakers feeding the transformer panels are rated at 25 amps. This requires #10 wire, we ran #12.  This needs to be corrected. This will require new #10 wire and ¾” flex conduit.  The ½” flex between the panels is OK.

- Wolf-tec has also requested that the 20 amp fuses that supply the breakers be changed out to 20 amp breakers.

Bill Boisvert

Bill Boisvert, Project Specialist

Avani Environmental Intl., Inc.®

95 Cypress Drive, Youngsville, North Carolina 27596

Cell: 919-971-3910 - Office: 919-488-5195

E-mail: bboisvert@avanienvironmental.com

An Absolent Group Company